Archbishop M.C. O’Neill
Asbestos Survey Report

Page 17

ARCHBISHOP M.C. O’NEILL HIGH SCHOOL

134 ARGYLE STREET
REGINA, SK.

ASBESTOS SURVEY REPORT

NOVEMBER 2010

Prepared For:
Regina Catholic School Division  

Prepared by:
Bersch & Associates Ltd.

Project No.:
R01.10

1.0
EXECUTIVE SUMMARY

The asbestos audit of Archbishop M.C. O’Neill High School located at 134 Argyle Street in Regina, SK. entailed the inspection of all accessible suspect asbestos-containing materials (ACM) located within the facility.  Materials inspected included mechanical equipment insulating material, suspended ceiling tile, vinyl floor coverings, cement counter tops, firestop material and transite rainwater leader.  As a result, asbestos was detected in the various areas of the facility. Accessible ACM within the facility has been clearly identified to eliminate uncertainty of asbestos content.  The identification of this material is as follows:
· All accessible asbestos-containing lineal pipe insulation located within the facility has been identified with “ASBESTOS” in red stencil.  All insulation on such lines shall be considered to be asbestos-containing or contaminated.   

· All accessible asbestos-containing pipefitting compound has been identified with a red dot of spray paint.  Such material may be found at, but may not be limited to, elbows, tees, hangers, expansions and valves.  

· Vessels that are insulated with asbestos-containing material are clearly labeled 'ASBESTOS' in red stencil.  All insulation on such vessels is to be considered asbestos or contaminated with asbestos.

· Asbestos-containing sheet vinyl floor was identified within various areas of the facility.  These areas have been identified on the attached floor plans.  

· The transite rainwater leaders located throughout the facility were found to contain asbestos.  Where accessible, these rainwater leaders have been labeled “ASBESTOS” in red stencil.  All transite rainwater leaders located within the facility shall be considered to be asbestos-containing.  

· Asbestos fume hood liner panels were identified within Room 212.  This material was not marked but persons conducting routine maintenance on the fume hoods shall be made aware of the presence of this material.  
· Asbestos counter top was identified within Rooms 205, 207, 210 and 212.  This material was not marked but persons conducting routine maintenance on the counter tops shall be made aware of the presence of this material.  

· Any material located within ceilings, wall cavities, pipe chases or other inaccessible areas or areas of limited access shall be considered asbestos-containing until testing of the material can determine the presence or absence of asbestos. 

· Please note that there is a potential for vermiculite insulation to be present within the block walls of the facility.  Vermiculite insulation has the potential to contain trace amounts of asbestos.  Therefore, any renovation activity that will require demolition of any portion of the perimeter block wall shall only be conducted after it has been determined that asbestos-containing vermiculite insulation is not present within the affected wall cavity.     

Please refer to Appendix I for Bulk Sample Analysis results.  

Throughout the survey of Archbisop M.C. O’Neill High School the asbestos-containing materials were assessed and given a Priority Rating of One, Two or Three, with Priority One being the items requiring the most attention.  

2.0
INTRODUCTION

Bersch & Associates Ltd. was retained by Regina Catholic School Board to conduct an asbestos audit of Archbishop M.C. O’Neill High School located at 134 Argyle Street.  The purpose of the survey was to identify all accessible Asbestos-Containing Materials (ACM) located within the facility and note any concerns relating to the ACM identified.  This report gives an account of the inspection and our firm’s recommendations on control options to be implemented to bring the facility in compliance with the Province of Saskatchewan Occupational Health and Safety Act and Regulations.  Bersch & Associates Ltd. completed the survey in November 2010.  

A review of this report shall be conducted with all trades that are entering the facility to perform maintenance or renovation activity.  This will ensure they are familiar with the types and locations of asbestos-containing materials present within the facility.  This will prevent any uncontrolled disturbance of the asbestos materials and possible exposure to asbestos.

3.0
METHODOLOGY

Bersch & Associates Ltd. began conducting the survey of the Archbishop M.C. O’Neill High School located at 134 Argyle Street. in June 2010.  The primary documents for guidance and criteria in this survey were the Province of Saskatchewan “Occupational Health and Safety Act and Regulations, 1996”, Province of Saskatchewan  “Managing Asbestos”, and the U.S. Environmental Protection Agency “Guidance for Controlling Asbestos Containing Materials in Buildings”.  The USEPA document identifies factors associated with the “condition” and the “potential for disturbance or erosion” of asbestos containing materials (ACM).  These factors help to determine potential for exposure to ACM and were used to make a qualitative evaluation of the material.  It should be noted that the recommendation of “Management” Asbestos Abatement Action is based upon the premise that renovations are not scheduled in that area that will require disturbing or violating the asbestos containing material.  In the event that renovations are scheduled that impact upon the areas of asbestos containing material then pre-removal of the asbestos containing materials may be necessary.  

In total, fifty-two (52) bulk samples of suspect asbestos-containing materials were collected within Archbishop M.C. O’Neill High School.  Refer to Appendix I for a copy of the Bulk Sample Analysis Report.  All bulk samples collected were analyzed by Bersch & Associates Ltd. laboratory in accordance with the current U.S. 40 CFR Part 763, Vol. 52, No.210 for the analysis of asbestos in building materials using polarized light microscopy and dispersion staining techniques.  The detection limit of this method is listed as greater than 1%.

4.0
RECOMMENDATIONS

The following information is a list of observations and recommendations with regards to the asbestos-containing materials identified within Archbishop M.C. O’Neill High School located at 134 Argyle Street.  

Priority One
Boiler Room
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located on the RH6 Line (Yellow) located South of the door to the Boiler Room.  Residual debris was noted on an end cap located approximately ten (10) feet from the doorway.  It is recommended that this material be removed to prevent further deterioration and potential dissemination of the asbestos-containing material.  
PRIORITY:




ONE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE

2. Pipefitting Compound - Asbestos was detected in the pipefitting compound located on the small diameter green line located between the boilers.  One (1) damaged fitting was noted on this line and is need of removal.  It is recommended that this fitting be removed to prevent further deterioration and potential dissemination of the asbestos-containing material.  
PRIORITY:




ONE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE

3. Pipefitting Compound - Asbestos was detected in the pipefitting compound located on the condensate line (Yellow) located adjacent the Maintenance Office.  One (1) damaged fitting was noted on this line along the South wall and is need of removal.  It is recommended that this fitting be removed to prevent further deterioration and potential dissemination of the asbestos-containing material.  
PRIORITY:




ONE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE

Fan Room B22

1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located on the lineal run located adjacent Vent Unit 1.  One fitting was noted in poor condition with missing portions.  It is recommended that this fitting be removed to prevent further deterioration and potential dissemination of the asbestos-containing material.  The remaining fittings in this area may be managed in place until renovations warrant removal.  
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE

Maintenance Work Shop
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Maintenance Work Shop.  One (1) damaged fitting was identified at the valve located approx. four (4) feet East of entrance.  It is recommended that this fitting be removed to prevent further deterioration and potential dissemination of the asbestos-containing material.  
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE

2. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Maintenance Work Shop.  One (1) damaged fitting was identified in the middle of the room (adjacent the duct).  It is recommended that this fitting be removed to prevent further deterioration and potential dissemination of the asbestos-containing material.  
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE

Basement Storage Room (adjacent Weight Room NW)
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Basement Storage Room.  One (1) damaged fitting was identified in the SE corner of the room.  It is recommended that this fitting be removed and that all residual debris located on the floor within the room be HEPA vacuumed to prevent further dissemination of the debris.  The remaining fittings in this area may be managed in place until renovations warrant removal.    
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
HIGH

ACTION:




REMOVE / CLEAN UP
Industrial Arts - Entrance
1. Light Fixture Heat Shield - Asbestos was detected in the heat shield material located within light fixtures located in the entrance room to the Industrial Arts Room.  The heat shield material is becoming dislodged from two (2) of the light fixtures.  It is recommended that all such fixtures be removed and replaced at earliest opportunity and the fixtures can be disposed of as asbestos waste.   
PRIORITY:




ONE

CONDITION:



MODERATE / POOR

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REMOVE / REPLACE
Industrial Arts Room 020
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Industrial Arts Room.  One (1) damaged fitting was identified in the middle of the room (above the sink).  It is recommended that this fitting be removed.
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
HIGH

ACTION:




REMOVE
2. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Industrial Arts Room.  One (1) damaged fitting was along the North wall of the room.  It is recommended that this fitting be removed.
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
HIGH

ACTION:




REMOVE
3. Pipefitting Compound – Loose pipefitting compound debris was noted on top of the duct adjacent the industrial Arts office.  It is recommended that the top of the duct be substantially cleaned up to remove all loose asbestos-containing debris.  
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
HIGH

ACTION:




REMOVE / CLEAN UP
Drama Room 28
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Drama Room.  A damaged fitting was noted along the East wall in the ceiling space.  It is recommended that this fitting be removed and that all residual debris located on the ceiling tile in this area be HEPA vacuumed.  The remaining fittings in this area may be managed in place until renovations warrant removal.    
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
HIGH

ACTION:




REMOVE / CLEAN UP
Basement Corridor (North-South)
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of the Basement Corridor.  Damaged fittings were noted at the North and South ends of the Corridor ceiling space.  It is recommended that these fittings be removed and that all residual debris located on the ceiling tile in these areas be HEPA vacuumed.  The remaining fittings in this area may be managed in place until renovations warrant removal.    
PRIORITY:




ONE

CONDITION:



POOR

POTENTIAL FOR DISTURBANCE:
HIGH

ACTION:




REMOVE / CLEAN UP
Priority Two

Boiler Room

1. Hot Water Tank Insulation - Asbestos was detected  in the insulation located on the Green Hot Water Tank in the Boiler Room.  Various repairs are required to the canvass to cover over exposed asbestos insulation.  It is recommended that the necessary repairs be completed to prevent further deterioration.  
PRIORITY:




TWO

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE / HIGH

ACTION:




REPAIR

Gymnasium 1 – Stage Area
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the Gym 1 – Stage Area.  A damaged fitting was identified on the roof drain line in the NE corner.  It is recommended that this fitting be repaired and the loose debris be HEPA vacuumed.  The remaining fittings in this area may be managed in place until renovations warrant removal.    
PRIORITY:




TWO

CONDITION:



MODERATE / POOR

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




REPAIR / CLEAN UP
Priority Three

Crawlspace
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within the Crawlspace.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Fan Room B22

1. Firestop Material - Asbestos was detected in the firestop material located in the NE corner wall penetration of the Fan Room.  Overall, this material was observed in moderate condition.  It is recommended that this material be managed in place until renovations warrant removal or the condition of the material deteriorates.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
2. Sheet Vinyl Floor - Asbestos was detected in the sheet vinyl floor located within Fan Room B22.  Overall, this material was observed in moderate condition.  It is recommended that this material be managed in place until renovations warrant removal or the condition of the material deteriorates.  Please note that there is a roll of sheet floor in storage in this area as well.  It is recommended that this material be taken out of service and disposed of at earliest convenience.    
PRIORITY:




THREE

CONDITION:



MODERATE
POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Basement Storage Room (adjacent Weight Room NW)

1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within the Basement Storage Room.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE
CONDITION:



GOOD
POTENTIAL FOR DISTURBANCE:
LOW
ACTION:




MANAGE

Classroom 015
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of Classroom 015.  Overall, these fittings were observed in moderate condition.  It is recommended that these fittings be managed in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
Industrial Arts - Classroom
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of the Industrial Arts Classroom.  Overall, these fittings were observed in moderate condition.  It is recommended that these fittings be managed in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
Industrial Arts - Office
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of the Industrial Arts Office.  Overall, these fittings were observed in moderate condition.  It is recommended that these fittings be managed in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
Industrial Arts – Wood Storage  / Paint Room
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of the Industrial Arts Wood Storage / Paint Room.  Overall, these fittings were observed in moderate condition.  It is recommended that these fittings be managed in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
Basement Washroom (Adj. Weight Room)
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of the Basement Washroom.  Overall, these fittings were observed in moderate condition.  It is recommended that these fittings be managed in place until renovations warrant removal.  Please note that many of these fittings are located above an enclosed ceiling and were not accessible for marking.    
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
Football Room / Team Locker Room
1. Pipefitting Compound - Asbestos was detected in the pipefitting compound located in the ceiling space of the Football Room / Team Locker Room.  Overall, these fittings were observed in moderate condition.  It is recommended that these fittings be managed in place until renovations warrant removal.  Please note that many of these fittings are located above an enclosed ceiling and were not accessible for marking.    
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
MODERATE

ACTION:




MANAGE
Student Commons Area

1. Sheet Vinyl Floor - Asbestos was detected in the sheet vinyl floor located within the Main Floor Student Commons Area.  Overall, this material was observed in moderate condition.  It is recommended that this material be managed in place until renovations warrant removal or the condition of the material deteriorates.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 150
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within Classroom 150.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Resource Centre
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within the Resource Centre.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Resource Centre - Office
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within the Resource Centre - Office.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Main Floor – Fan Room (Adj. Old Gym Storage)
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within the Main Floor Fan Room.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Main Floor – Girl’s Washroom (Adj. Student Commons)
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within the Main Floor Girl’s Washroom.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Please note that this material is located above an enclosed ceiling and was not accessible for marking.    
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Gymnasium 2
1. Transite Rainwater Leader - Asbestos-containing transite rainwater leader was identified within Gymnasium 2.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Please note that this material was not accessible for marking.    
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 205
1. Counter Top (White) - Asbestos-containing counter top was identified in Classroom 205.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Due to the high visibility of this material, it was left unmarked.  All counter top in this room shall be considered to be asbestos-containing.      
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 207
1. Counter Top (White) - Asbestos-containing counter top was identified in Classroom 207.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Due to the high visibility of this material, it was left unmarked.  All counter top in this room shall be considered to be asbestos-containing.      
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 210
1. Counter Top (White) - Asbestos-containing counter top was identified in Classroom 210.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Due to the high visibility of this material, it was left unmarked.  All counter top in this room shall be considered to be asbestos-containing.      
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 212
1. Counter Top (White) - Asbestos-containing counter top was identified in Classroom 212.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Due to the high visibility of this material, it was left unmarked.  All counter top in this room shall be considered to be asbestos-containing.      
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 212
1. Fume Hood Liner Panel - Asbestos-containing fume hood liner panel was identified within Classroom 212.  The liner panel is located on the interior walls of the fume hood.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Due to the high visibility of this material, it was left unmarked.  All fume hood liner panel in this room shall be considered to be asbestos-containing.      
PRIORITY:




THREE

CONDITION:



GOOD

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

Classroom 240
1. Sheet Vinyl Floor - Asbestos was detected in the sheet vinyl floor located within Classroom 240.  Overall, this material was observed in moderate condition.  It is recommended that this material be managed in place until renovations warrant removal or the condition of the material deteriorates.  
PRIORITY:




THREE

CONDITION:



MODERATE

POTENTIAL FOR DISTURBANCE:
LOW

ACTION:




MANAGE

The remaining asbestos-containing materials identified within the facility (not listed above) may be managed in place until renovations warrant removal.  

5.0
ASBESTOS ABATEMENT DISCUSSION

Asbestos is a known carcinogen and is listed in the Province of Saskatchewan under the Occupational Health and Safety Appendix, Part V as a Hazardous Chemical Substance and any release of asbestos fibres into the atmosphere creates a potential health hazard.  Although the mechanism and epidemiology of asbestos carcinogenisis is not yet well defined, accumulating evidence suggests the significance of exposure at even very low fibre concentrations and hence human exposure should be kept to a minimum.  It should be noted however that asbestos is a natural mineral and a measurable background concentration can be detected in any location sampled (inside buildings, outside buildings, urban, rural, etc.).  The recommendations of the report are therefore intended to keep the potential exposure to an absolute minimum with the knowledge that a zero exposure is not possible.

Asbestos containing materials have been used in a wide variety of applications.  Of particular concern, is the group of so called friable products.  A friable product is one which can be crumbled or reduced to powder or smaller fragments by hand pressure.  Publications from the U.S.E.P.A. as early as 1977 have indicated the potential hazard of asbestos exposure in buildings containing these friable products.  The two main uses of friable asbestos products are as spray insulation (thermal, acoustic or fireproofing) on deck and/or beams or as thermal insulation on piping or mechanical equipment.  A large amount of non-friable asbestos-containing materials have also been used in building construction such as asbestos cement board and asbestos containing vinyl flooring.

The mere presence of a friable asbestos containing material does not imply that there is an actual presence of elevated airborne fibre.  As numerous studies have indicated, elevated asbestos fibre levels are generally found when settled dust or the actual asbestos containing material itself is disturbed by maintenance, renovation, inadvertent contact or vibration.  The factors considered in the Environmental Protection Agency (USEPA) exposure assessment (condition of material, water damage, activity, movement, exposed surface area, accessibility, friability and presence in an air stream) often give some indication of the likelihood of fibre release but are not in any way definitive in determining whether a hazard exists or not.  That is, even if the most friable product exists in a building, elevated fibre levels will not likely occur unless there is some disturbance by physical contact, vibration or an air stream.  

There are four possible approaches to control exposure to airborne asbestos once a friable material is identified in a building.  These methods briefly are as follows:

A) Removal - Asbestos material is removed and disposed of by burial and replaced by non-asbestos materials.

B) Encapsulation - Asbestos material is coated with a bridging or penetrating sealant. 

C) Enclosure - Asbestos containing materials are separated from the building environment by barriers such as suspended ceilings or cladding materials.

D)
Deferred Action or Management and Custodial Control - The Province of Saskatchewan Human Resources, Labor and Employment Branch under the Occupational health and Safety Regulations publish a document outlining “The Management of Asbestos”.  In the guide for compliance, an action plan is outlined for management of the asbestos materials identified and in summary is:

3. Identification, which has been accomplished by this report.

2. Development of Written Handling Procedures for maintenance personnel or often arrangements are made for a qualified contractor to conduct the necessary removal or spot maintenance prior to the regular staff conducting maintenance.

3. Asbestos Abatement Awareness and Process Training if the regular maintenance personnel are required to conduct asbestos related activities.

4.
Inspection on regular basis is conducted to determine the ongoing condition of the material.

For the specifics of this report Removal, Repair and Management of the asbestos containing materials are the recommended planned activities.  Removal of the asbestos containing material observed in poor condition is the only solution to provide permanent elimination of any potential for airborne fibre release.  In the event of renovations or maintenance to areas containing asbestos materials, written procedures must be developed to conduct the activity or prior removal if the situation warrants.

6.0
REFERENCES 

.1 Province of Saskatchewan  "The Occupational Health and Safety Act and The Occupational Health and Safety Regulations" Office Consolidation, December 1996. 

.2 Province of Saskatchewan Human Resources, Labor, and Employment  "The Management of Asbestos" January, 1991.

.3 USEPA, U.S. Environmental Protection Agency, "Guidance for Controlling Asbestos-Containing Materials in Buildings". Washington, DC: Office of Toxic Substances, USEPA.
