Dr. Martin Leboldus
Asbestos Survey Report

Page 2

DR. MARTIN LEBOLDUS HIGH SCHOOL

 2330 – 25TH AVENUE
REGINA, SK.

ASBESTOS SURVEY REPORT

NOVEMBER 2010

Prepared For:
Regina Catholic School Division  

Prepared by:
Bersch & Associates Ltd.

Project No.:
R01.10

1.0
EXECUTIVE SUMMARY

The asbestos audit of Dr. Martin Leboldus High School located at 2330 – 25th Avenue in Regina, SK. entailed the inspection of all accessible suspect asbestos-containing materials (ACM) located within the facility.  Materials inspected included mechanical equipment insulating material, suspended ceiling tile, vinyl floor coverings, fume hood panels and transite rainwater leader.  As a result, asbestos was detected in the various areas of the facility. Accessible ACM within the facility has been clearly identified to eliminate uncertainty of asbestos content.  The identification of this material is as follows:
· All accessible asbestos-containing pipefitting compound has been identified with a red dot of spray paint.  Such material may be found at, but may not be limited to, elbows, tees, hangers, expansions and valves.  
· All accessible asbestos-containing lineal pipe insulation located within the facility has been identified with “ASBESTOS” in red stencil.  All insulation on such lines shall be considered to be asbestos-containing or contaminated.   

· Vessels that are insulated with asbestos-containing material are clearly labeled 'ASBESTOS' in red stencil.  All insulation on such vessels is to be considered asbestos or contaminated with asbestos.
· The transite rainwater leaders located throughout the facility were found to contain asbestos.  Where accessible, these rainwater leaders have been labeled “ASBESTOS” in red stencil.  Please note that some sections of the transite pipe located within the ceiling space of the Second Floor Corridor were not accessible for marking at the time of our inspection.  All transite rainwater leaders located within the facility shall be considered to be asbestos-containing.   
· Asbestos-containing fume hood panels were identified within Room 271.  This material has not been marked due to the high visibility of the material.  It is recommended that any person conducting routine maintenance on the fume hood be made aware of the presence of this material.  
· Any material located within ceilings, wall cavities, pipe chases or other inaccessible areas or areas of limited access shall be considered asbestos-containing until testing of the material can determine the presence or absence of asbestos. 

· Please note that there is a potential for vermiculite insulation to be present within the block walls.  Vermiculite insulation has the potential to contain trace amounts of asbestos.  Therefore, any renovation activity that will require demolition of any portion of a block wall shall only be conducted after it has been determined that asbestos-containing vermiculite insulation is not present within the affected wall cavity.     

Please refer to Appendix I for Bulk Sample Analysis results.  

Throughout the survey Dr. Martin Leboldus High School the asbestos-containing materials were assessed and given a Priority Rating of One, Two or Three, with Priority One being the items requiring the most attention.  

2.0
INTRODUCTION

Bersch & Associates Ltd. was retained by Regina Catholic School Division to conduct an asbestos audit of Dr. Martin Leboldus High School located at 2330 – 25th Avenue.  The purpose of the survey was to identify all accessible Asbestos-Containing Materials (ACM) located within the facility and note any concerns relating to the ACM identified.  This report gives an account of the inspection and our firm’s recommendations on control options to be implemented to bring the facility in compliance with the Province of Saskatchewan Occupational Health and Safety Act and Regulations.  Bersch & Associates Ltd. completed the survey in November 2010.  

A review of this report shall be conducted with all trades that are entering the facility to perform maintenance or renovation activity.  This will ensure they are familiar with the types and locations of asbestos-containing materials present within the facility.  This will prevent any uncontrolled disturbance of the asbestos materials and possible exposure to asbestos.

3.0
METHODOLOGY

Bersch & Associates Ltd. began conducting the survey of Dr. Martin Leboldus High School located at 2330 – 25th Avenue  in June 2010.  The primary documents for guidance and criteria in this survey were the Province of Saskatchewan “Occupational Health and Safety Act and Regulations, 1996”, Province of Saskatchewan  “Managing Asbestos”, and the U.S. Environmental Protection Agency “Guidance for Controlling Asbestos Containing Materials in Buildings”.  The USEPA document identifies factors associated with the “condition” and the “potential for disturbance or erosion” of asbestos containing materials (ACM).  These factors help to determine potential for exposure to ACM and were used to make a qualitative evaluation of the material.  It should be noted that the recommendation of “Management” Asbestos Abatement Action is based upon the premise that renovations are not scheduled in that area that will require disturbing or violating the asbestos containing material.  In the event that renovations are scheduled that impact upon the areas of asbestos containing material then pre-removal of the asbestos containing materials may be necessary.  

In total, thirty-six (36) bulk samples of suspect asbestos-containing materials were collected within Dr. Martin Leboldus High School.  Refer to Appendix I for a copy of the Bulk Sample Analysis Report.  All bulk samples collected were analyzed by Bersch & Associates Ltd. laboratory in accordance with the current U.S. 40 CFR Part 763, Vol. 52, No.210 for the analysis of asbestos in building materials using polarized light microscopy and dispersion staining techniques.  The detection limit of this method is listed as greater than 1%.

4.0
RECOMMENDATIONS

The following information is a list of observations and recommendations with regards to the asbestos-containing materials identified within Dr. Martin Leboldus High School located at 2330 – 25th Avenue.  
Priority One
Crawlspace
1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within the Crawlspace.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  Although the transite pie is considered to be non-friable, a number of broken pieces/sections were identified on the floor area of the Crawlspace.  It is recommended that the Crawlspace be thoroughly cleaned in the immediate vicinity of all in-place transite rainwater leader and all loose transite pipe debris be removed from the floor area of the Crawlspace.    

PRIORITY:




ONE

CONDITION:




POOR

POTENTIAL FOR DISTURBANCE:

MODERATE
ACTION:





CLEAN UP
Priority Two
Boiler Room
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located within the Boiler Room.  A damaged fitting was noted on the blue line located adjacent the hot water storage tanks.  It is recommended that this fitting be repaired to prevent further deterioration and potential uncontrolled fibre release.  
PRIORITY:




TWO

CONDITION:




MODERATE / POOR

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





REPAIR
2. Vessel Insulation – Asbestos was detected in the insulation located on the green hot water tank in the Boiler Room.  In general, the material was observed in good condition.  However, a few minor repairs are necessary to canvass jacketing on the tank.  It is recommended that all exposed areas on the tank are properly repaired with canvass to prevent further deterioration.   
PRIORITY:




TWO
CONDITION:




MODERATE / POOR

POTENTIAL FOR DISTURBANCE:

MODERATE
ACTION:





REPAIR
Priority Three
Second Floor Corridor

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within the Second Floor Corridor.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Please note that much of this material was not accessible for marking at the time of our inspection.     

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 270

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within Room 270.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 260
1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within Room 260.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 250 (Chapel)

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within Room 250 (Chapel).  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 240 (Resource Centre)

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within Room 240 (Resource Centre).  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
North Stairwell

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within the North Stairwell.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  Please note that this material was not accessible for marking at the time of our inspection.    

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 110 (Drama)

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within Room 110 (Drama).  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 110 (2nd Level Fan Room)

1. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within Room 110 (2nd Level Fan Room).  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
Room 271

1. Fume Hood Liner Panel – Asbestos-containing fume hood liner panel was identified within Room 271.  This material is affixed to the interior of the fume hood walls.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE – INSPECT ANNUAL
The remaining asbestos-containing materials identified within the facility may be managed in place until renovations warrant removal.  

5.0
ASBESTOS ABATEMENT DISCUSSION

Asbestos is a known carcinogen and is listed in the Province of Saskatchewan under the Occupational Health and Safety Appendix, Part V as a Hazardous Chemical Substance and any release of asbestos fibres into the atmosphere creates a potential health hazard.  Although the mechanism and epidemiology of asbestos carcinogenisis is not yet well defined, accumulating evidence suggests the significance of exposure at even very low fibre concentrations and hence human exposure should be kept to a minimum.  It should be noted however that asbestos is a natural mineral and a measurable background concentration can be detected in any location sampled (inside buildings, outside buildings, urban, rural, etc.).  The recommendations of the report are therefore intended to keep the potential exposure to an absolute minimum with the knowledge that a zero exposure is not possible.

Asbestos containing materials have been used in a wide variety of applications.  Of particular concern, is the group of so called friable products.  A friable product is one which can be crumbled or reduced to powder or smaller fragments by hand pressure.  Publications from the U.S.E.P.A. as early as 1977 have indicated the potential hazard of asbestos exposure in buildings containing these friable products.  The two main uses of friable asbestos products are as spray insulation (thermal, acoustic or fireproofing) on deck and/or beams or as thermal insulation on piping or mechanical equipment.  A large amount of non-friable asbestos-containing materials have also been used in building construction such as asbestos cement board and asbestos containing vinyl flooring.

The mere presence of a friable asbestos containing material does not imply that there is an actual presence of elevated airborne fibre.  As numerous studies have indicated, elevated asbestos fibre levels are generally found when settled dust or the actual asbestos containing material itself is disturbed by maintenance, renovation, inadvertent contact or vibration.  The factors considered in the Environmental Protection Agency (USEPA) exposure assessment (condition of material, water damage, activity, movement, exposed surface area, accessibility, friability and presence in an air stream) often give some indication of the likelihood of fibre release but are not in any way definitive in determining whether a hazard exists or not.  That is, even if the most friable product exists in a building, elevated fibre levels will not likely occur unless there is some disturbance by physical contact, vibration or an air stream.  

There are four possible approaches to control exposure to airborne asbestos once a friable material is identified in a building.  These methods briefly are as follows:

A) Removal - Asbestos material is removed and disposed of by burial and replaced by non-asbestos materials.

B) Encapsulation - Asbestos material is coated with a bridging or penetrating sealant. 

C) Enclosure - Asbestos containing materials are separated from the building environment by barriers such as suspended ceilings or cladding materials.

D)
Deferred Action or Management and Custodial Control - The Province of Saskatchewan Human Resources, Labor and Employment Branch under the Occupational health and Safety Regulations publish a document outlining “The Management of Asbestos”.  In the guide for compliance, an action plan is outlined for management of the asbestos materials identified and in summary is:

3. Identification, which has been accomplished by this report.

2. Development of Written Handling Procedures for maintenance personnel or often arrangements are made for a qualified contractor to conduct the necessary removal or spot maintenance prior to the regular staff conducting maintenance.

3. Asbestos Abatement Awareness and Process Training if the regular maintenance personnel are required to conduct asbestos related activities.

4.
Inspection on regular basis is conducted to determine the ongoing condition of the material.

For the specifics of this report Removal, Repair and Management of the asbestos containing materials are the recommended planned activities.  Removal of the asbestos containing material observed in poor condition is the only solution to provide permanent elimination of any potential for airborne fibre release.  In the event of renovations or maintenance to areas containing asbestos materials, written procedures must be developed to conduct the activity or prior removal if the situation warrants.
6.0
REFERENCES 

.1 Province of Saskatchewan  "The Occupational Health and Safety Act and The Occupational Health and Safety Regulations" Office Consolidation, December 1996. 

.2 Province of Saskatchewan Human Resources, Labor, and Employment  "The Management of Asbestos" January, 1991.

.3 USEPA, U.S. Environmental Protection Agency, "Guidance for Controlling Asbestos-Containing Materials in Buildings". Washington, DC: Office of Toxic Substances, USEPA.
