| ### Sample | Date Sampled | Start Time | End Time | Volume L/M | ## Activity | ## Location | ### Fibers per cc. | ## Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 39 | 29/07/15 | 08:17 | 15:44 | 0.586 | South Concourse – Textured Ceiling Abatement | Decontamination Facility - Clean Room | 0.0047 | Fibre Level Acceptable. No Concerns Noted. |
| 40 | 29/07/15 | 08:18 | 15:45 | 0.687 | South Concourse – Textured Ceiling Abatement | Adjacent Decontamination Clean Room | 0.0042 | Fibre Level Acceptable. No Concerns Noted. |
| 41 | 29/07/15 | 08:19 | 15:46 | 0.591 | South Concourse – Textured Ceiling Abatement | Gymnasium | 0.0028 | Fibre Level Acceptable. No Concerns Noted. |
| 42 | 29/07/15 | 08:20 | 15:47 | 0.513 | South Concourse – Textured Ceiling Abatement | West Corridor Adjacent Room 190 | 0.0021 | Fibre Level Acceptable. No Concerns Noted. |
| 43 | 29/07/15 | 08:21 | 15:48 | 0.429 | South Concourse – Textured Ceiling Abatement | East Corridor Adjacent Room 157 | 0.0026 | Fibre Level Acceptable. No Concerns Noted. |

Analyzed as per NIOSH 7400 Method for Sampling and Evaluating Airborne Asbestos Dust / Asbestos Fibre Counting - NIOSH 582E.  Occupational Health & Safety of the Province of Saskatchewan regulations state where an asbestos process has been completed the air monitoring must verify that airborne asbestos fibre concentrations are less than 0.01 fibres per cubic centimeter of air.