[image: image1.wmf]
Air Monitoring Bulletin
Miller Comprehensive High School
1027 College Avenue

Regina, SK.  

Project No. R01.12
July 27, 2012

	Sample
	Date

Sampled
	Start

Time
	End

Time
	Activity
	Location
	Fibers

per cc.
	Comments

	1

	07/27/12
	17:00
	20:00

	Woodworking Shop – Air Clearance Following Asbestos Abatement
	Woodworking Shop – Inside Work Enclosure
	0.0005
	Fibre Level Acceptable.

Air Clearance Granted.

	2


	07/27/12
	17:00
	20:00


	Woodworking Shop – Air Clearance Following Asbestos Abatement
	Woodworking Shop – Inside Work Enclosure
	0.0007
	Fibre Level Acceptable.

Air Clearance Granted.


Note:  
Air samples were analyzed in accordance with the NIOSH 7400 Standard Method which is the accepted method in the Province of Saskatchewan.  Occupational Health & Safety of the Province of Saskatchewan has established a clearance level of 0.01 fibres/cc. following an asbestos process.  
Trent Blaus

Bersch & Associates Ltd.


[image: image1.wmf]_945285652

