| ### Sample | Date Sampled | Start Time | End Time | Volume L/M | ## Activity | ## Location | ### Fibers per cc. | ## Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 36 | 28/07/15 | 10:01 | 13:15 | 2.142 | ILS – Mezzanine Mechanical Room Clean-up | ILS Room – Adjacent Work Enclosure | 0.0030 | Fibre Level Acceptable. No Concerns Noted. |
| 37 | 28/07/15 | 13:11 | 15:44 | 3.587 | ILS – Mezzanine Mechanical Room Air Clearance | ILS – Mezzanine Mechanical Room – Inside Work Enclosure | 0.0013 | Fibre Level Acceptable. No Concerns Noted. |
| 38 | 28/07/15 | 13:12 | 15:45 | 3.368 | ILS – Mezzanine Mechanical Room Air Clearance | ILS – Mezzanine Mechanical Room – Inside Work Enclosure | 0.0019 | Fibre Level Acceptable. No Concerns Noted. |

Analyzed as per NIOSH 7400 Method for Sampling and Evaluating Airborne Asbestos Dust / Asbestos Fibre Counting - NIOSH 582E.  Occupational Health & Safety of the Province of Saskatchewan regulations state where an asbestos process has been completed the air monitoring must verify that airborne asbestos fibre concentrations are less than 0.01 fibres per cubic centimeter of air.