St. Matthew School

Asbestos Survey Report

Page 12

[image: image1.jpg]



ST. MATTHEW SCHOOL
 4710 CASTLE ROAD
REGINA, SK.

ASBESTOS SURVEY REPORT
OCTOBER 2012
Prepared For:
Regina Catholic School Division  

Prepared by:
Bersch & Associates Ltd.

Project No.:
R01.12
1.0
EXECUTIVE SUMMARY

The asbestos audit of St. Matthew School located at 4710 Castle Road in Regina, SK. entailed the inspection of all accessible suspect asbestos-containing materials (ACM) located within the facility.  Materials inspected included mechanical equipment insulating material, suspended ceiling tile, vinyl floor coverings, duct expansion canvass and transite rainwater leader.  As a result, asbestos was detected in the various areas of the facility. Accessible ACM within the facility has been clearly identified to eliminate uncertainty of asbestos content.  The identification of this material is as follows:
· All accessible asbestos-containing pipefitting compound has been identified with a red dot of spray paint.  Such material may be found at, but may not be limited to, elbows, tees, hangers, expansions and valves.  
· Asbestos-containing lineal pipe insulation was identified in various areas throughout the facility.  Where accessible, this material has been clearly labelled “ASBESTOS” in red stencil.  All insulation on such lines shall be considered to contain asbestos or be asbestos-contaminated.  

· Asbestos transite rainwater leader was identified in various areas of the facility.  Where accessible, this material has been clearly labelled “ASBESTOS” in red stencil.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing until testing can prove otherwise.  
· Asbestos-containing firestop material was identified within the Basement at various wall penetrations.  Caution should be taken when conducting mechanical work that may disturb this material.  This material has been identified with red spray paint.  
· Vinyl asbestos floor tile was identified in various locations throughout the facility.
· Asbestos sheet flooring was identified within the Nurse’s Room.  

· Please note that, at the time of our inspection, no access into Classroom 15 or the South Storage Room was provided.  Therefore, any suspect materials located within these rooms shall be considered to be asbestos-containing until testing can prove otherwise.  
· Please note that asbestos-containing vermiculite may be present within the facility.  Vermiculite insulation has the potential to contain trace amounts of asbestos.  Therefore, any renovation activity that will require demolition of any portion of a block wall shall only be conducted after it has been determined that asbestos-containing vermiculite insulation is not present within the affected wall cavity.     

· Any material located within ceilings, wall cavities, pipe chases or other inaccessible areas or areas of limited access shall be considered asbestos-containing until testing of the material can determine the presence or absence of asbestos. 
Please refer to Appendix I for Bulk Sample Analysis results.  

Throughout the survey of St. Matthew School, the asbestos-containing materials were assessed and given a Priority Rating of One, Two or Three, with Priority One being the items requiring the most attention.  
2.0
INTRODUCTION

Bersch & Associates Ltd. was retained by Regina Catholic School Division to conduct an asbestos audit of St. Matthew School located at 4710 Castle Road in Regina, SK.  The purpose of the survey was to identify all accessible Asbestos-Containing Materials (ACM) located within the facility and note any concerns relating to the ACM identified.  This report gives an account of the inspection and our firm’s recommendations on control options to be implemented to bring the facility in compliance with the Province of Saskatchewan Occupational Health and Safety Act and Regulations.  Bersch & Associates Ltd. completed the survey in October 2012.  

A review of this report shall be conducted with all trades that are entering the facility to perform maintenance or renovation activity.  This will ensure they are familiar with the types and locations of asbestos-containing materials present within the facility.  This will prevent any uncontrolled disturbance of the asbestos materials and possible exposure to asbestos. 
3.0
METHODOLOGY

Bersch & Associates Ltd. began conducting the survey of St. Matthew School located at 4710 Castle Road in Regina, SK. in July 2012.  The primary documents for guidance and criteria in this survey were the Province of Saskatchewan “Occupational Health and Safety Act and Regulations, 1996”, Province of Saskatchewan  “Managing Asbestos”, and the U.S. Environmental Protection Agency “Guidance for Controlling Asbestos Containing Materials in Buildings”.  The USEPA document identifies factors associated with the “condition” and the “potential for disturbance or erosion” of asbestos containing materials (ACM).  These factors help to determine potential for exposure to ACM and were used to make a qualitative evaluation of the material.  It should be noted that the recommendation of “Management” Asbestos Abatement Action is based upon the premise that renovations are not scheduled in that area that will require disturbing or violating the asbestos containing material.  In the event that renovations are scheduled that impact upon the areas of asbestos containing material then pre-removal of the asbestos containing materials may be necessary.   
In total, twenty-three (23) bulk samples of suspect asbestos-containing materials were collected within St. Matthew School.  Refer to Appendix I for a copy of the Bulk Sample Analysis Report.  All bulk samples collected were analyzed by Bersch & Associates Ltd. laboratory in accordance with the current U.S. 40 CFR Part 763, Vol. 52, No.210 for the analysis of asbestos in building materials using polarized light microscopy and dispersion staining techniques.  The detection limit of this method is listed as greater than 1%.

4.0
RECOMMENDATIONS

The following information is a list of observations and recommendations with regards to the asbestos-containing materials identified within St. Matthew School located at 4710 Castle Road in Regina, SK.  
Priority One 
Crawlspace -  Removed/Cleaned Summer 2017
1. Lineal Pipe Insulation – Asbestos was detected in the lineal pipe insulation located within the Crawlspace.  Numerous damaged sections were noted during our inspection.  In addition, loose asbestos debris was noted on the ground in various locations.  It is our recommendation that all damaged sections of lineal pipe insulation be removed and all loose debris located on the ground be cleaned up.  (It may be more cost effective to remove all asbestos-containing insulation from the Crawlspace at this time).  
PRIORITY:




ONE

CONDITION:




MODERATE / POOR

POTENTIAL FOR DISTURBANCE:

MODERATE / HIGH

ACTION:





REMOVE / CLEAN-UP
Multi-Purpose Area - Removed Summer 2017
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located within the Ceiling Space of the Multi-Purpose area.  The roof drain fitting has been damaged and debris is present atop of the ceiling tiles.  It is our recommendation that the remaining pipefitting compound on the roof drain line be removed and that the top side of the ceiling tiles be cleaned.   
PRIORITY:




ONE
CONDITION:




MODERATE / POOR
POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





REMOVE / CLEAN-UP
Gymnasium - Removed Summer 2017
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located on the roof drain line in the Gymnasium.  The roof drain fitting has been damaged.  It is our recommendation that this fitting be removed.   
PRIORITY:




ONE
CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





REMOVE
Basement - Removed Summer 2017
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located within the Basement.  One damaged fitting, overhead adjacent cement beam, was noted.  It is recommended that this fitting be removed.    
PRIORITY:




ONE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





REMOVE
Priority Three
Basement
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located within the Basement.  Overall, the fittings were observed in moderate condition.  The remaining fittings may be managed in place until renovations warrant removal or the condition of the material deteriorates.     
PRIORITY:




THREE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
2. Firestop – Asbestos was detected in the firestop material located at pipe penetrations within the Basement.  In general, this material was observed in moderate condition.  This material may be managed in place until renovations warrant removal or the condition of the material deteriorates.     
PRIORITY:




THREE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
Nurse’s Room
1. Sheet Vinyl Floor – Asbestos was detected in the sheet vinyl floor backing material located in the Nurse’s Room.  The asbestos is present within the backing material which allows the vinyl face to act as a barrier to prevent disturbance of the asbestos.  The vinyl flooring was observed in moderate condition and may be managed in place until renovations warrant removal or the condition of the material deteriorates.  
PRIORITY:




THREE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
Kindergarten Room
1. Sheet Vinyl Floor – Asbestos was detected in the sheet vinyl floor backing material located in the Kindergarten Room.  The asbestos is present within the backing material which allows the vinyl face to act as a barrier to prevent disturbance of the asbestos.  The vinyl flooring was observed in moderate condition and may be managed in place until renovations warrant removal or the condition of the material deteriorates.  
PRIORITY:




THREE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
South Corridor
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located within the Ceiling Space of the South Corridor.  Overall, the fittings were observed in moderate condition.  These fittings may be managed in place until renovations warrant removal or the condition of the material deteriorates.     
PRIORITY:




THREE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
North Corridor
1. Pipefitting Compound – Asbestos was detected in the pipefitting compound located within the Ceiling Space of the North Corridor.  Overall, the fittings were observed in moderate condition.  These fittings may be managed in place until renovations warrant removal or the condition of the material deteriorates.     
PRIORITY:




THREE

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
2. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified within the North Corridor.  All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  
PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
Storage Room (Adjacent VP Office)
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Storage Room adjacent the VP Office.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Room 12
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in Room 12.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Room 13
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in Room 13.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Caretaker’s Closet
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Caretaker’s Closet.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Storage Room (Adjacent Gymnasium)

1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Storage Room adjacent the Gymnasium.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Gymnasium Storage
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Gymnasium Storage Room.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Storage Room Adjacent Room 4
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Storage Room adjacent Room 4.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Caretaker’s Closet Adjacent Room 8
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Caretaker’s Closet adjacent Room 8.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Storage Room Adjacent Room 9
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Storage Room adjacent Room 9.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

Caretaker’s Storage Room
1.
Vinyl Floor Tile (9”x9”) - Asbestos was detected in the 9” x 9” vinyl floor tile located in the Caretaker’s Storage Room.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE
Multi-Purpose Corridor
1.
Vinyl Floor Tile (12” x 12”) - Asbestos was detected in the 12” x 12” vinyl floor tile located in the Multi-Purpose Corridor.  The flooring in this area was observed in moderate condition.  This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




MODERATE


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





MANAGE

The remaining asbestos-containing materials identified within the facility may be managed in place until renovations warrant removal.  

5.0
ASBESTOS ABATEMENT DISCUSSION

Asbestos is a known carcinogen and is listed in the Province of Saskatchewan under the Occupational Health and Safety Appendix, Part V as a Hazardous Chemical Substance and any release of asbestos fibres into the atmosphere creates a potential health hazard.  Although the mechanism and epidemiology of asbestos carcinogenisis is not yet well defined, accumulating evidence suggests the significance of exposure at even very low fibre concentrations and hence human exposure should be kept to a minimum.  It should be noted however that asbestos is a natural mineral and a measurable background concentration can be detected in any location sampled (inside buildings, outside buildings, urban, rural, etc.).  The recommendations of the report are therefore intended to keep the potential exposure to an absolute minimum with the knowledge that a zero exposure is not possible.

Asbestos containing materials have been used in a wide variety of applications.  Of particular concern, is the group of so called friable products.  A friable product is one which can be crumbled or reduced to powder or smaller fragments by hand pressure.  Publications from the U.S.E.P.A. as early as 1977 have indicated the potential hazard of asbestos exposure in buildings containing these friable products.  The two main uses of friable asbestos products are as spray insulation (thermal, acoustic or fireproofing) on deck and/or beams or as thermal insulation on piping or mechanical equipment.  A large amount of non-friable asbestos-containing materials have also been used in building construction such as asbestos cement board and asbestos containing vinyl flooring.

The mere presence of a friable asbestos containing material does not imply that there is an actual presence of elevated airborne fibre.  As numerous studies have indicated, elevated asbestos fibre levels are generally found when settled dust or the actual asbestos containing material itself is disturbed by maintenance, renovation, inadvertent contact or vibration.  The factors considered in the Environmental Protection Agency (USEPA) exposure assessment (condition of material, water damage, activity, movement, exposed surface area, accessibility, friability and presence in an air stream) often give some indication of the likelihood of fibre release but are not in any way definitive in determining whether a hazard exists or not.  That is, even if the most friable product exists in a building, elevated fibre levels will not likely occur unless there is some disturbance by physical contact, vibration or an air stream.  

There are four possible approaches to control exposure to airborne asbestos once a friable material is identified in a building.  These methods briefly are as follows:

A) Removal - Asbestos material is removed and disposed of by burial and replaced by non-asbestos materials.

B) Encapsulation - Asbestos material is coated with a bridging or penetrating sealant. 

C) Enclosure - Asbestos containing materials are separated from the building environment by barriers such as suspended ceilings or cladding materials.

D)
Deferred Action or Management and Custodial Control - The Province of Saskatchewan Human Resources, Labor and Employment Branch under the Occupational health and Safety Regulations publish a document outlining “The Management of Asbestos”.  In the guide for compliance, an action plan is outlined for management of the asbestos materials identified and in summary is:

3. Identification, which has been accomplished by this report.

2. Development of Written Handling Procedures for maintenance personnel or often arrangements are made for a qualified contractor to conduct the necessary removal or spot maintenance prior to the regular staff conducting maintenance.

3. Asbestos Abatement Awareness and Process Training if the regular maintenance personnel are required to conduct asbestos related activities.

4.
Inspection on regular basis is conducted to determine the ongoing condition of the material.

For the specifics of this report Removal, Repair and Management of the asbestos containing materials are the recommended planned activities.  Removal of the asbestos containing material observed in poor condition is the only solution to provide permanent elimination of any potential for airborne fibre release.  In the event of renovations or maintenance to areas containing asbestos materials, written procedures must be developed to conduct the activity or prior removal if the situation warrants.
6.0
REFERENCES 

.1 Province of Saskatchewan  "The Occupational Health and Safety Act and The Occupational Health and Safety Regulations" Office Consolidation, December 1996. 

.2 Province of Saskatchewan Human Resources, Labor, and Employment  "The Management of Asbestos" January, 1991.

.3 USEPA, U.S. Environmental Protection Agency, "Guidance for Controlling Asbestos-Containing Materials in Buildings". Washington, DC: Office of Toxic Substances, USEPA.
