St. Peter School

Asbestos Survey Report

Page 20

[image: image1.jpg]



ST. PETER SCHOOL
 150 ARGYLE STREET
REGINA, SK.

ASBESTOS SURVEY REPORT
May 2013
Prepared For:
Regina Catholic School Division  

Prepared by:
Bersch & Associates Ltd.

Project No.:
R01.13
1.0
EXECUTIVE SUMMARY

The asbestos audit of St. Peter School located at 150 Argyle Street in Regina, SK. entailed the inspection of all accessible suspect asbestos-containing materials (ACM) located within the facility.  Materials inspected included mechanical equipment insulating material, suspended ceiling tile, vinyl floor coverings, various other building materials, and transite rainwater leader.  As a result, asbestos was detected in the various areas of the facility. Accessible ACM within the facility has been clearly identified to eliminate uncertainty of asbestos content.  The identification of this material is as follows:
· All accessible asbestos-containing pipefitting compound has been identified with a red dot of spray paint.  Such material may be found at, but may not be limited to, elbows, tees, hangers, expansions and valves.
· The mud compound on the insulated water tank was identified with a red “ASBESTOS” stencil.
·   Duct expansion gasket was identified with a red dot of spray paint.
· Asbestos-containing fire stop material has been identified with a red dot of spray paint. 
· Asbestos vinyl floor tiles were identified within the facility.  These areas have been identified on the attached floor plans. This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).
· The transite rainwater leaders located throughout the facility were found to contain asbestos.  Where accessible, these rainwater leaders have been labeled “ASBESTOS” in red stencil.  All transite rainwater leaders located within the facility shall be considered to be asbestos-containing.  
· The heat shield material within the light fixtures have been identified in this report. 

· The beige painted boards around the window sills were not sampled but may contain asbestos. Consider these boards to be ACM, or have a sample taken at the time renovations that will require disturbance of the material. These boards will not be mentioned on a room by room basis.  
· The fire door entry door to the boiler room may contain asbestos. 

· There may be asbestos duct expansion gasket below the yellow insulation on the mechanical ducting.

· Material located within ceilings, wall cavities, pipe chases or other inaccessible areas or areas of limited access shall be considered asbestos-containing until testing of the material can determine the presence or absence of asbestos. 

· Please note that there is a potential for vermiculite insulation to be present within the block walls.  Vermiculite insulation has the potential to contain trace amounts of asbestos.  Therefore, any renovation activity that will require demolition of any portion of a block wall shall only be conducted after it has been determined that asbestos-containing vermiculite insulation is not present within the affected wall cavity.     

Please refer to Appendix I for Bulk Sample Analysis results.  

Throughout the survey of St. Peter School, the asbestos-containing materials were assessed and given a Priority Rating of One, Two or Three, with Priority One being the items requiring the most attention.  
Bersch & Associates Ltd. implemented the use of door jamb labels that are applied to every door jamb within the facility.  This permits anyone accessing the room to easily identify the ACM present without having to reference the written report.  Legend identifying explanation of abbreviations used on door jambs will be placed on back doors of all maintenance/custodial rooms.  Employees and contractors will use the legend as a reference to identify ACM within the areas they are working.  

2.0
INTRODUCTION

Bersch & Associates Ltd. was retained by Regina Catholic School Division to conduct an asbestos audit of St. Peter School located at 150 Argyle Street.  The purpose of the survey was to identify all accessible Asbestos-Containing Materials (ACM) located within the facility and note any concerns relating to the ACM identified.  This report gives an account of the inspection and our firm’s recommendations on control options to be implemented to bring the facility in compliance with the Province of Saskatchewan Occupational Health and Safety Act and Regulations.  Bersch & Associates Ltd. completed the survey in May 2013.  

A review of this report shall be conducted with all trades that are entering the facility to perform maintenance or renovation activity.  This will ensure they are familiar with the types and locations of asbestos-containing materials present within the facility.  This will prevent any uncontrolled disturbance of the asbestos materials and possible exposure to asbestos. 
3.0
METHODOLOGY

Bersch & Associates Ltd. began conducting the survey of St. Peter School located at 150 Argyle Street in May 2013.  The primary documents for guidance and criteria in this survey were the Province of Saskatchewan “Occupational Health and Safety Act and Regulations, 1996”, Province of Saskatchewan  “Managing Asbestos”, and the U.S. Environmental Protection Agency “Guidance for Controlling Asbestos Containing Materials in Buildings”.  The USEPA document identifies factors associated with the “condition” and the “potential for disturbance or erosion” of asbestos containing materials (ACM).  These factors help to determine potential for exposure to ACM and were used to make a qualitative evaluation of the material.  It should be noted that the recommendation of “Management” Asbestos Abatement Action is based upon the premise that renovations are not scheduled in that area that will require disturbing or violating the asbestos containing material.  In the event that renovations are scheduled that impact upon the areas of asbestos containing material then pre-removal of the asbestos containing materials may be necessary.  

In total, twenty-five (25) bulk samples of suspect asbestos-containing materials were collected within St. Peter School.  Refer to Appendix I for a copy of the Bulk Sample Analysis Report.  All bulk samples collected were analyzed by Bersch & Associates Ltd. laboratory in accordance with the current U.S. 40 CFR Part 763, Vol. 52, No.210 for the analysis of asbestos in building materials using polarized light microscopy and dispersion staining techniques.  The detection limit of this method is listed as greater than 1%.

4.0
RECOMMENDATIONS

The following information is a list of observations and recommendations with regards to the asbestos-containing materials identified within St. Peter School located at 150 Argyle Street.  
Priority One
Boiler Room - Removed Summer 2017
1. Pipeline Fitting Compound– Damaged pipeline fittings have been observed within the Boiler Room in poor condition. Our recommendations is to either remove/ repair two damaged fittings adjacent the hot water heater, and one at valve handle above the cement stairs.    

PRIORITY:




ONE

CONDITION:




POOR

POTENTIAL FOR DISTURBANCE:

HIGH

ACTION:





REPAIR/ REMOVE
Corridor adjacent Classrooms 300, 301, 302 
1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Corridor.  The flooring in this area was observed in poor condition. Replace damaged floor tiles with new non-asbestos tiles. 
PRIORITY:




ONE


CONDITION:




POOR


POTENTIAL FOR DISTURBANCE:

MODERATE

ACTION:





REPLACE

Corridor adjacent Classrooms 305, 306, 307  - Removed Summer 2017
1. Pipeline Fitting Compound- Pipeline fittings were observed within the Corridor. Remove damaged fittings above ceiling tile, adjacent 306 entry door.

PRIORITY:




ONE

CONDITION:




POOR

POTENTIAL FOR DISTURBANCE:

HIGH

ACTION:





REMOVE

Second Floor Corridor - Removed Summer 2017
1. Pipeline Fitting Compound – Pipeline fittings were observed within the Second Floor Corridor. Remove ruminated of fitting above ceiling tile, 25’ from Classroom 306 entry door. 

PRIORITY:




ONE

CONDITION:




POOR

POTENTIAL FOR DISTURBANCE:

HIGH

ACTION:





REMOVE

Caretaker Mechanical Room - Removed Summer 2017
1. Pipeline Fitting Compound- Pipeline fittings were observed within the Mechanical Room. Remove damaged fitting coming off of insulated tank in the corner of room and clean up debris below tank.
PRIORITY:




ONE

CONDITION:




POOR

POTENTIAL FOR DISTURBANCE:

HIGH

ACTION:





REMOVE/ CLEAN UP

2. Mud Compound- Asbestos mud compound was observed within the Mechanical Room. Repair canvass on white insulated tank in the corner of room, where the canvass is damaged. 
PRIORITY:




ONE

CONDITION:




POOR

POTENTIAL FOR DISTURBANCE:

HIGH

ACTION:





REPAIR

Storage Room (below center stairs) - Removed Summer 2017
1. Vinyl Floor Tiles- There is a box of asbestos 9” by 9” floor tiles that can be disposed of. (the door jamb for this room says N/A)
Priority Two
Lobby
1. Heat Shield Material- Asbestos heat shield material has been identified within the light fixtures of the lobby. Remove light fixtures if damaged.
PRIORITY:




TWO

CONDITION:




MODERATE

POTENTIAL FOR DISTURBANCE:

HIGH

ACTION:





REMOVE

Priority Three
Boiler Room
1. Fire Stop Material– Asbestos fire stop material was detected within the Boiler Room.  The material has been observed in good condition. This material may be managed in place until renovations warrant removal.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom P02

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom P09

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 102

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 105
1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 108

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 109

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 110
1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW
ACTION:





MANAGE

Classroom 111

-May have asbestos vinyl floor tiles below carpet.

Classroom 204

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 301
1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 302

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 305

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 306

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 307

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 307 Washroom
 1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Washroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Classroom 308

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Classroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Room 303

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Room.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Room 303- Broadcasting Room

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Broadcasting Room.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Room 303- Computer Room

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Computer Room.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Room 303- Storage Room

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Storage Room.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Girl’s Washroom adjacent 301

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Washroom.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Caretaker Closet

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Closet. The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Caretaker Office

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Office.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

2. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified in the Office. All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
Lobby
1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Lobby. The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

2. Pipeline Fitting Compounds- Pipeline fittings were observed within the lobby but were inaccessible to label due to the height of the ceiling. Consider these fittings to be ACM.

PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Gym

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Gym. The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
*The drain pipe and drain pipe fittings within the gym were inaccessible to identify. Consider them to ACM unless proven otherwise. 

First Floor Corridor

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Corridor. The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
2. Pipeline Fitting Compound- Pipeline fittings were observed above the ceiling tile within the corridor. These fittings were observed in good condition. The fittings in this area may be managed in place until renovations warrant removal. 
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
Second Floor Corridor

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Corridor.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Corridor adjacent Classroom 305, 306, 307

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Corridor.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Center Stairwell

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Stairwell.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Dressing and Physical Education Room

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Storage Room. The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Storage Room adjacent Classroom 204, 205

1.
 Vinyl Floor Tiles - Asbestos was detected in the vinyl floor tiles located in the Storage Room.  The flooring in this area was observed in good condition.  This material may be managed in place until renovations warrant removal.  The location of this material has been identified on the floor plans attached in Appendix II.
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE

Nurse
1. Pipeline Fitting Compound- Pipeline fittings were observed within the Nurse Room above the ceiling tile. These fittings were observed in good condition. The fittings in this area may be managed in place until renovations warrant removal. 
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
*The door jamb is marked FTG, VSF, the VSF should be disregarded as the sheet flooring contains no asbestos. 

Upstairs Fan Room

1. Pipeline Fitting Compound- Pipeline fittings were observed within the Fan Room. These fittings were observed in good condition. The fittings in this area may be managed in place until renovations warrant removal. 
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
2. Duct Expansion Gasket- Asbestos duct expansion gasket was observed within the fan room. The gasket was observed in good condition and may be managed in place until renovations warrant removal. 
PRIORITY:




THREE


CONDITION:




GOOD


POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
3. Transite Rainwater Leader – Asbestos-containing transite rainwater leader was identified in the Office. All transite rainwater leader located within the facility shall be considered to be asbestos-containing.  This material is considered non-friable and will not produce an elevated fibre release unless rigorously disturbed (i.e. cutting, grinding, smashing, etc.).  It is recommended that this material remain in place until renovations warrant removal.  

PRIORITY:




THREE

CONDITION:




GOOD

POTENTIAL FOR DISTURBANCE:

LOW

ACTION:





MANAGE
The remaining asbestos-containing materials identified within the facility may be managed in place until renovations warrant removal.  

5.0
ASBESTOS ABATEMENT DISCUSSION

Asbestos is a known carcinogen and is listed in the Province of Saskatchewan under the Occupational Health and Safety Appendix, Part V as a Hazardous Chemical Substance and any release of asbestos fibres into the atmosphere creates a potential health hazard.  Although the mechanism and epidemiology of asbestos carcinogenisis is not yet well defined, accumulating evidence suggests the significance of exposure at even very low fibre concentrations and hence human exposure should be kept to a minimum.  It should be noted however that asbestos is a natural mineral and a measurable background concentration can be detected in any location sampled (inside buildings, outside buildings, urban, rural, etc.).  The recommendations of the report are therefore intended to keep the potential exposure to an absolute minimum with the knowledge that a zero exposure is not possible.

Asbestos containing materials have been used in a wide variety of applications.  Of particular concern, is the group of so called friable products.  A friable product is one which can be crumbled or reduced to powder or smaller fragments by hand pressure.  Publications from the U.S.E.P.A. as early as 1977 have indicated the potential hazard of asbestos exposure in buildings containing these friable products.  The two main uses of friable asbestos products are as spray insulation (thermal, acoustic or fireproofing) on deck and/or beams or as thermal insulation on piping or mechanical equipment.  A large amount of non-friable asbestos-containing materials have also been used in building construction such as asbestos cement board and asbestos containing vinyl flooring.

The mere presence of a friable asbestos containing material does not imply that there is an actual presence of elevated airborne fibre.  As numerous studies have indicated, elevated asbestos fibre levels are generally found when settled dust or the actual asbestos containing material itself is disturbed by maintenance, renovation, inadvertent contact or vibration.  The factors considered in the Environmental Protection Agency (USEPA) exposure assessment (condition of material, water damage, activity, movement, exposed surface area, accessibility, friability and presence in an air stream) often give some indication of the likelihood of fibre release but are not in any way definitive in determining whether a hazard exists or not.  That is, even if the most friable product exists in a building, elevated fibre levels will not likely occur unless there is some disturbance by physical contact, vibration or an air stream.  

There are four possible approaches to control exposure to airborne asbestos once a friable material is identified in a building.  These methods briefly are as follows:

A) Removal - Asbestos material is removed and disposed of by burial and replaced by non-asbestos materials.

B) Encapsulation - Asbestos material is coated with a bridging or penetrating sealant. 

C) Enclosure - Asbestos containing materials are separated from the building environment by barriers such as suspended ceilings or cladding materials.

D)
Deferred Action or Management and Custodial Control - The Province of Saskatchewan Human Resources, Labor and Employment Branch under the Occupational health and Safety Regulations publish a document outlining “The Management of Asbestos”.  In the guide for compliance, an action plan is outlined for management of the asbestos materials identified and in summary is:

3. Identification, which has been accomplished by this report.

2. Development of Written Handling Procedures for maintenance personnel or often arrangements are made for a qualified contractor to conduct the necessary removal or spot maintenance prior to the regular staff conducting maintenance.

3. Asbestos Abatement Awareness and Process Training if the regular maintenance personnel are required to conduct asbestos related activities.

4.
Inspection on regular basis is conducted to determine the ongoing condition of the material.

For the specifics of this report Removal, Repair and Management of the asbestos containing materials are the recommended planned activities.  Removal of the asbestos containing material observed in poor condition is the only solution to provide permanent elimination of any potential for airborne fibre release.  In the event of renovations or maintenance to areas containing asbestos materials, written procedures must be developed to conduct the activity or prior removal if the situation warrants.
6.0
REFERENCES 

.1 Province of Saskatchewan  "The Occupational Health and Safety Act and The Occupational Health and Safety Regulations" Office Consolidation, December 1996. 

.2 Province of Saskatchewan Human Resources, Labor, and Employment  "The Management of Asbestos" January, 1991.

.3 USEPA, U.S. Environmental Protection Agency, "Guidance for Controlling Asbestos-Containing Materials in Buildings". Washington, DC: Office of Toxic Substances, USEPA.
